- General Requirements

- Furnish and install ___ (qty) packaged, modulating, sealed combustion, high efficiency gas-fired boiler(s) with stainless steel vertical firetube heat exchanger design

- ___(qty) Weil-McLain SVF 3000 commercial high efficiency, packaged water boiler(s) capable of burning natural gas or propane gas

- Boiler(s) shall have no less than a 3000 MBH maximum input rating, 2874 MBH gross output rating and 2499 net AHRI MBH at 100% fire rate

- Boiler(s) shall be no less than 95.8% combustion efficiency AHRI certified

- Boiler(s) shall be capable of full modulation firing with a minimum 8.3:1 turn down ratio for natural gas and propane applications

- Boiler(s) shall be capable of passage through a standard 36” wide door-fit

- Boiler(s) will include a maximum allowable working pressure of no less than 160 psig

- Boiler(s) shall have no less than a ratio of 19.3 BTUs Gross Output/Gallon of water stored in the boiler to protect the heat exchanger from variances in gallons per minute flow rates

- Boiler(s) shall be capable of zero clearance to combustion boiler room installation

- Boiler(s) dimensions shall not exceed any of the following dimensions:  84.4” length, 35.2” width, and 79.1” height

- Boiler(s) to be installed in accordance with the manufacturer’s installation instructions with all work to conform to plumbing industry standards

- Product

- Acceptable boiler manufacturer(s) must

  - Comply with specifying engineer’s requirements and meet the full intent of the project(s) design specifications

  - Provide complete submittal including literature, manuals, wiring diagrams, fuel piping diagrams and access to electronic revit files; Any alternate must be of equivalent performance, size and footprint, piping configuration, clearance requirements and heating surface

  - Provide bid submittal to engineer by requested date or at least seven working days in advance  of bid opening for approval; substitutions are not permitted after award of contract

- Boiler Construction

- Boiler(s) heat exchanger must include

  - Vertical firetube design

  - 316L stainless steel tube/tube sheet and condensate tray and 304 stainless heat exchanger shell make of material

  - Fire testing and hydrostatical pressure testing at the factory in accordance with ASME requirements

  - Alternating, opposed indentation firetube geometry for maximum heat transfer

  - Serviceable condensate tray to capture heat exchanger and vent system condensate with removable design that does not require heat exchanger disassembly

  - Counter-balanced / hinged cover-plate design

  - Cooled cover-plate design to redirect heat back in to the heat exchanger and minimize external temperature

  - Barrel nut cover-plate to heat exchanger bolt design

  - Cover-plate hatch for quick access to burner and heat exchanger

  - Access to the heat exchanger combustion chamber and fire tubes for wash down service that shall not require heat exchanger disassembly

- Factory assembly and testing

- Boiler(s) main components:

  - The boiler cover plate shall include a hinged design to allow for easy access to the heat exchanger internal components and require a maximum of 18” overhead clearance from top of boiler

  - Integrated roller casters to enable boiler removal from the shipping crate, transport to the boiler installation site and boiler positioning without the need for a lift jack or fork lift

  - Integrated leveling legs to mitigate the need for a dedicated concrete boiler pad/surface

  - Boiler(s) shall be supplied with a gas valve designed with negative pressure regulation (fan venturi effect “pulls” gas through the valve rather than gas pressure “pushing” gas through the valve); Negative pressure regulation enables the boiler to operate in a safe condition at the minimum allowable inlet pressure; The inlet gas (natural gas or propane) pressure to the boiler valve shall be at a minimum of 3.5 inches water column and maximum of 14 water column

  - The burner shall include a premix combustion design, made with stainless steel and a woven metal fiber outer covering to provide a wide range of modulating firing rates

  - The boiler(s) shall be equipped with a device capable of controlling the air/fuel ratio through a 10:1 turn for natural gas and propane applications.

  - Maximum 3” flanged water supply and return line manifolds and connections

  - Fully removable, steel boiler jacket panels with rugged steel frame with commercial powder coat

  - True sealed cabinet design in which heat radiant heat is redirected into the heat exchanger to maximize operating efficiency

  - Industrial grade push button control display

  - The control system shall have an electronic display for boiler set-up wizard, boiler status, boiler diagnostics and typical heating system presets

  - A pleated canister-style intake air filter with Filter Minder system to enable user to monitor filter dirtiness / clogged condition

  - Dual cover plate site glassed spark flame rod and flame visible from either side of boiler

  - Dual pressure and temperature gauge taps on both sides of the supply water manifold

  - Tapping on return water manifold to accommodate a flow switch

  - Tapping on the supply water manifold for the relief valve to mitigate need in downline external piping

- Venting and Combustion Air

- Boiler(s) must be capable of using outside air piped directly to the boiler for combustion; Inlet and termination of these pipes must be connected to either sidewall or through-the-roof wall terminations as recommended by the manufacturer

- The boiler shall be direct vent or direct exhaust capable certified with the following vent materials:  PVC, CPVC, PP, or SS (AL29-4)

- Vent/air connection to be 10" in diameter

- Vent runs up to 100’ maximum allowable length with minimum allowable vent length of 10'

- Boiler(s) to be capable of:  direct exhaust - vertical (Category II), direct vent – sidewall, vertical, and side intake with vertical exhaust (Category IV), direct exhaust – vertical (Category IV)

- Common venting is achievable as a Category II system according to the boiler manual installation instructions and common venting installation parameters found in the application guide.

- Boiler Trim

- All electrical components to be of high quality and bear UL label

- Direct spark ignition

- 50 VA transformer

- Boiler(s) electrical requirement not to exceed 16.3 full load amps and shall accommodate a 208 volt / 3 phase / 60 hertz power source

- CSD-1 compliant with factory test report for ASME CSD-1

- Standard boiler(s) controls to include:

  - High limit temperature control with manual reset (210 degree F maximum allowable boiler water temperature)

  - Operating limit temperature control (190 degree F maximum set-point)

  - Combination pressure-temperature gauge; Gauge dial clearly marked and easily read

  - Standard, factory supplied, 30 psi ASME certified pressure relief valve with option to 50/80/100/150 pressure relief valve

  - Supply & return system to include ½” NPT X4” immersion style water temperature sensors with option to strap-on style

  - Low water cut-off protection with manual reset

  - High and low gas pressure switches with manual reset and indicator lights

  - Outdoor temperature sensor

- Boiler Controller to include:

- An express set-up wizard and fully customizable options

- Operating status color LCD display

- Standard Modbus connectivity with option to BACnet and Lonworks

- Preset operating parameters including typical heating systems

- Configurable outdoor reset

- Rate setting for each input / output

- Contact with 0-10v output

- 0-10 input (modulation or set-point)

- Labeled terminal blocks for field terminations

- Ignition control

- High limit and modulating temperature control

- Alarm control functionality

- Onboard time and date

- Low water cut off

- Manual reset

- Warm weather shutdown

- Freeze protection

- Boiler service interval and contractor information

- (3) 120V powered outputs/2.2 amps max each, (1) dry contact/10 amps max

- Outdoor temperature reset and warm weather shutdown

- Variable temperature zones that require no mixing valves

- Multiplex LCD digital temperature access points including supply, return, system temperatures, and flue gas temperature

- Alarm contacts that include flame fail, high temperature and low water control cut off

- Multiple boiler functionality to include:

  - Up to 8 boiler cascading / lead lag operation and boiler rotation for equal run hours

  - Series, parallel, or SmartTM sequencing

  - Lead boiler rotation

  - Variable primary flow design capable

  - Three boilers priority capability:  either (2) network and (1) local or (1) Network and (2) local

  - (24) Zone inputs and outputs with 8 total cascaded boilers via Zone StackingTM

  - Auxiliary inputs  - flow and end switches

  - System auxiliary outputs for system pump or damper

- Boiler Manuals

- The boiler(s) shall be provided with complete instruction manuals including:

  - Boiler Installation Manual

  - User Manual

  - Advanced Manual

- Boiler Packaging

  - Shall include an integrated shipping ramp to allow for removal from shipping crate and positioning up on to an existing boiler pad without the need for a forklift

- Certifications and Regulatory Compliance

- Boiler(s) shall include ASME, AHRI, CSA listing and/or approvals

- Boiler(s) shall be manufactured to conform to ASME Section IV Boiler and Pressure Vessel Code

- CSD-1 compliant:  manual reset low water cut-off, manual reset high and low gas pressure switches, UL 353 certified high limit control with manual reset, and UL 353 certified operating control

- Certified to appliance code ANSI Z21.13 / CSA 4.9 gas-fired low pressure steam and hot water boilers

- Boiler(s) shall have an independent laboratory rating of <30 ppm Corr. 3%O2 Nitrogen Oxides (NOx) emissions